## wire run chart
5 KW WIRE RUN CHART
for 1.5% energy losses in 5 m/s average
tower height, feet (6awg) | 60 | 80 | 100 | 120 | 140
ohms down tower | 0.024528 | 0.032704 | 0.04088 | 0.049056 | 0.057232
total phase ohms | 0.087 | 0.087 | 0.087 | 0.087 | 0.087
wire run ohms | 0.062472 | 0.054296 | 0.04612 | 0.037944 | 0.029768
AWG | wire run distance to base of tower (feet)
6 | 150 | 130 | 110 | 90 | 70
4 | 240 | 210 | 180 | 150 | 120
3 | 310 | 270 | 230 | 190 | 150
2 | 390 | 340 | 290 | 230 | 180
0 | 610 | 534.4094 | 453.937 | 373.4646 | 292.9921
for 3% energy losses in 5 m/s average
tower height, feet (6awg) | 60 | 80 | 100 | 120 | 140 | AWG | ohms/1000'
ohms down tower | 0.024528 | 0.032704 | 0.04088 | 0.049056 | 0.057232 | 8 | 0.6498
total phase ohms | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 6 | 0.4088
wire run ohms | 0.15047 | 0.1423 | 0.13412 | 0.12594 | 0.11777 | 4 | 0.2571
[6 empty] | 3 | 0.2039
AWG | wire run distance to base of tower (feet) |  |  |  |  | 2 | 0.1617
8 | 230 | 220 | 210 | 190 | 180 | 0 | 0.1016
6 | 370 | 350 | 330 | 310 | 290 | 00 | 0.0798
4 | 590 | 550 | 520 | 490 | 460 | 000 | 0.0633
3 | 740 | 700 | 660 | 620 | 580
2 | 930 | 880 | 830 | 780 | 730
0 | 1480 | 1400.5512 | 1320.0787 | 1239.6063 | 1159.1339
for 6% energy losses in 5 m/s average
tower height, feet (6awg) | 60 | 80 | 100 | 120 | 140
ohms down tower | 0.024528 | 0.032704 | 0.04088 | 0.049056 | 0.057232
total phase ohms | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
wire run ohms | 0.32547 | 0.3173 | 0.30912 | 0.30094 | 0.29277
AWG | wire run distance to base of tower (feet)
8 | 500 | 490 | 480 | 460 | 450
6 | 800 | 780 | 760 | 740 | 720
4 | 1270 | 1230 | 1200 | 1170 | 1140
3 | 1600 | 1560 | 1520 | 1480 | 1440
2 | 2010 | 1960 | 1910 | 1860 | 1810
0 | 3200 | 3122.9921 | 3042.5197 | 2962.0472 | 2881.5748

## 5kW-S WindCAD
WindCad Turbine Performance Model
BWC 5kW, Grid - Intertie |  |  |  | Tier/neo-SH3055-6.2m
Prepared For: | SWCC
Site Location: | Reference |  |  |  |  | tested with 28m awg 6and
Data Source: | AWEA Standard |  |  |  |  | 58.5 m #1
Date: | 2011-09-26 10:22
Inputs: |  | Results:
Ave. Wind (m/s) = | 5 |  | Hub Average Wind Speed (m/s) = | 5 |  | AWG | ohms/1000'
Weibull K = | 2 |  | Air Density Factor = | 0% |  | 0 | 0.1016
Site Altitude (m) = | 0 |  | Average Output Power (kW) = | 1.1172 |  | 00 | 0.0798
Wind Shear Exp. = | 0.2 |  | Daily Energy Output (kWh) = | 26.8127 |  | 000 | 0.0633
Anem. Height (m) = | 28 |  | Annual Energy Output (kWh) = | 9786.6301 |  | 1 | 0.1282
Tower Height (m) = | 28 |  | Monthly Energy Output = | 815.5525 |  | 2 | 0.1617
Distance to Tower (m) = | 40 |  | Percent Operating Time = | 85.31% |  | 3 | 0.2039
Tower Wire (AWG) | 6 |  | Total Phase Resistance Ω = | 0.091179 |  | 4 | 0.2571
Wire Run (AWG) = | 6 |  | Annual Total kWh Wire Loss= | 155.4134 |  | 6 | 0.4088
Turbulence Factor = | 0% |  | wire loss = | 1.563% |  | 8 | 0.6498
Weibull Performance Calculations | [5 empty] | weibull c | 5.6451
Wind Speed Bin (m/s) | Power (kW) | Wind Probability (f) | Net kWh @ V | wire loss kW | Net kWh loss |  | average RPM
1 | -0.0055119 | 3.035% | -1.4655 | 0 | 0 | 1 | 0
1.5 | -0.0055119 | 4.378% | -2.1139 | 0 | 0 | 1.5 | 0
2 | -0.0055119 | 5.526% | -2.6681 | 0 | 0 | 2 | 24.1127
2.5 | 0.029118 | 6.437% | 16.4186 | 0 | 0 | 2.5 | 32.7928
3 | 0.089009 | 7.086% | 55.2542 | 0.0011905 | 0.73901 | 3 | 44.3899
3.5 | 0.20042 | 7.467% | 131.0986 | 0.0021576 | 1.4113 | 3.5 | 59.8969
4 | 0.32112 | 7.587% | 213.4339 | 0.0033517 | 2.2277 | 4 | 72.6386
4.5 | 0.48751 | 7.471% | 319.0763 | 0.0051846 | 3.3933 | 4.5 | 86.3496
5 | 0.70562 | 7.153% | 442.1698 | 0.0079612 | 4.9888 | 5 | 100.9006
5.5 | 0.89668 | 6.675% | 524.3164 | 0.010569 | 6.1803 | 5.5 | 111.1137
6 | 1.2438 | 6.081% | 662.5524 | 0.015789 | 8.4106 | 6 | 126.4556
6.5 | 1.5932 | 5.416% | 755.8908 | 0.021694 | 10.2924 | 6.5 | 139.4352
7 | 1.9679 | 4.721% | 813.7604 | 0.028647 | 11.8461 | 7 | 151.5276
7.5 | 2.3455 | 4.03% | 827.9763 | 0.036468 | 12.8736 | 7.5 | 162.7251
8 | 2.7225 | 3.372% | 804.0871 | 0.04484 | 13.2433 | 8 | 172.9718
8.5 | 3.1246 | 2.766% | 757.1217 | 0.054603 | 13.2311 | 8.5 | 183.4877
9 | 3.6127 | 2.226% | 704.6006 | 0.067188 | 13.1039 | 9 | 195.657
9.5 | 4.0099 | 1.759% | 617.7669 | 0.077913 | 12.0034 | 9.5 | 205.3553
10 | 4.4558 | 1.364% | 532.3458 | 0.090728 | 10.8395 | 10 | 216.73
10.5 | 4.8633 | 1.039% | 442.4724 | 0.10414 | 9.4751 | 10.5 | 229.2809
11 | 5.287 | 0.7769% | 359.7948 | 0.11623 | 7.9094 | 11 | 243.1693
11.5 | 5.6083 | 0.5709% | 280.4562 | 0.12304 | 6.153 | 11.5 | 258.445
12 | 5.8178 | 0.4122% | 210.0631 | 0.12159 | 4.3902 | 12 | 269.5417
12.5 | 5.9825 | 0.2925% | 153.2785 | 0.10543 | 2.7012 | 12.5 | 286.7108
13 | 6.0436 | 0.204% | 107.9921 | 0 | 0 | 13 | 302.0745
13.5 | 6.1001 | 0.1398% | 74.7288 | 0 | 0 | 13.5 | 317.6092
14 | 6.1362 | 0.09425% | 50.6644 | 0 | 0 | 14 | 333.0154
14.5 | 6.0931 | 0.06246% | 33.3372 | 0 | 0 | 14.5 | 348.2236
15 | 5.9964 | 0.0407% | 21.3774 | 0 | 0 | 15 | 352.7533
15.5 | 5.9895 | 0.02608% | 13.6815 | 0 | 0 | 15.5 | 371.52
16 | 6.1338 | 0.01643% | 8.8288 | 0 | 0 | 16 | 398.2167
16.5 | 6.297 | 0.01018% | 5.6169 | 0 | 0 | 16.5 | 413.525
17 | 6.3485 | 0.006207% | 3.4516 | 0 | 0 | 17 | 387.1
17.5 | 6.3 | 0.003721% | 2.0535 | 0 | 0 | 17.5 | 400
18 | 6.0533 | 0.002194% | 1.1636 | 0 | 0 | 18 | 383.0333
18.5 | 6.3 | 0.001273% | 0.70252 | 0 | 0 | 18.5 | 400
19 | 6.362 | 0.0007264% | 0.40486 | 0 | 0 | 19 | 417
19.5 | 6.362 | 0.0004078% | 0.22729 | 0 | 0 | 19.5 | 417
20 | 6.362 | 0.0002253% | 0.12554 | 0 | 0 | 20 | 417
2011, BWC | Totals: | 98.25% | 9942.0435 |  | 155.4134
Weibull Calculations: Wind speed probability is calculated as a Weibull curve defined by the average wind speed and a shape factor, K. To facilitate piece-wise integration, the wind speed range is broken down into "bins" of 1 m/s in width (Column 1). For each wind speed bin, instantaneous wind turbine power (W, Column 2)) is multiplied by the Weibull wind speed probability (f, Column 3). This cross product (Net W, Column 4) is the contribution to average turbine power output contributed by wind speeds in that bin. The sum of these contributions is the average power output of the turbine on a continuous, 24 hour, basis. Best results are achieved using annual or monthly average wind speeds. Use of daily or hourly average speeds is not recommended. Wire Run Losses: AWG 6 is supplied for armored cable tower wire runs from BWC. Tower wire run typically underground in conduit. Keep inverter near grid connection to avoid difficulties with grid side overvoltage errors ! ! ! ! ! !
Instructions: Inputs: Use annual or monthly Average Wind speeds. If Weibull K is not known, use K = 2 for inland sites, use 3 for coastal sites, and use 4 for island sites and trade wind regimes. Site Altitude is meters above sea level. Wind Shear Exponent is best assumed as 0.18. For rough terrain or high turbulence use 0.22. For very smooth terrain or open water use 0.11. Anemometer Height is for the data used for the Average Wind speed. If unknown, use 10 meters. Tower Height is the nominal height of the tower, eg.: 24 meters. Turbulence Factor is a derating for turbulence, site variability, and other performance influencing factors -- typical turbulence has already been incorporated into the model. Use 0.00 (0%) for level sites with limited obstructions. Use -0.10 ( negative 10%) for flat, clear sites on open water. Use 0.05 to 0.15 (5% to 15%) for rolling hills or mountainous terrain. Results: Hub Average Wind Speed is corrected for wind shear and used to calculate the Weibull wind speed probability. Air Density Factor is the reduction from sea level performance. Average Power Output is the average continuous equivalent output of the turbine. Daily Energy Output is the average energy produced per day. Annual and Monthly Energy Outputs are calculated using the Daily value. Percent Operating Time is the time the turbine should be producing some power. Limitations: This model uses a mathmatical idealization of the wind speed probability. The validity of this assumption is reduced as the time period under consideration (ie, the wind speed averaging period) is reduced. This model is best used with annual or monthly average wind speeds. Use of this model with daily or hourly average wind speed data is not recommended because the wind will not follow a Weibull distribution over short periods. The data used in creating the power curve was generated at the BWC test site in Norman, OK. Consult Bergey Windpower Co. for special needs. Your performance may vary.
5 kW